PLANS REVIEW CHECK LIST – PUBLIC POOL –DOH / BOAF version May 3, 2012

Date_____________

County________________________________ Date Received_______________ Log#_____________

Project______________________________________________________________________________

Engineer__________________________________ Original____ Revision____ Modification____

Reviewed By_______________________________ SP-_______________________File #__________

Date Re-Submittal Received:________________ Date of 2nd Review:______________________

_____________________________________________________________________________________

Items needing correction or clarification are marked by an "X" beside the appropriate section number of the Florida Administrative Code citation (2009 64E-9, FAC, or 2010 FBC 424.1).  We have left the 64E-9 requirements in this checklist because they are critical for public health and therefore the pool will be checked for these items by the County Health Department at the first operating permit inspection after the Building Official’s approval of the construction.

Reviewer:  Note that section 424.1.8.1 requires that “Spa pools shall meet the requirement of Sections 424.1.1 through 424.1.6.5, unless specifically indicated otherwise.”  Use the additional “Spa pool” checklist for spa pools.  This checklist can be used for Wading pools and there is an additional Wading pool detail checklist.

From: www.myfloridaeh.com/water/swim/index.html

Florida Building Code or		  #sets plans  _____disk____

Florida Administrative Code
Section
	SwP    Spa/WaP

64E-9.005(1)(a)3.	____	___/___	Plans review fees received as required by Section 64E-9.015.

64E-9.005(1)(a)	____ 	___/___	Six one-piece applications for approval of swimming pool plans received.

64E-9.005(1)(a)	____ 	___/___	Six sets of signed and sealed engineering plans received (proper size).

64E-9.005(1)(a)2.	____ 	___/___	A 4" x 6" blank space exists on lower right hand corner of plans sheets; site plan is included.

64E-9.005(1)(a)2.	____ 	___/___	An equipment list and specifications with manufacturer and/or distributor
	     		names, model numbers, and catalog numbers included on plans.

424.1.2.1(a)  	____ 	___/___	Pool constructed of impervious structurally rigid material, light in color, with a smooth, non-toxic, 
	     		slip-resistant finish. 

424.1.2.3.2	____ 	___/___	Pool shell free of designs which interfere with detection of human(s) in distress, algae, sediment, 
	     		or other objects in pool.

424.1.6.5.3.2.5	____ 	___/___	A min. 4” tile line (6” for skimmer pools) is at the water line, max. 12” if dark tile. Gutter pools may 
                                    		use 2” tile line along pool wall edge of gutter lip. (tiles are min. 1” on all sides)  

424.1.2.1 (b) 	____ 	___/___	If 1” tiles are used in pool, adhesive is certified for shear strength (250 psi) & underwater use. 

424.1.2.3.3 &.4	____ 	___/___	Lap lanes and targets on non-competition pools to meet code. (2-6” wide markings)

424.1.1	____ 	___/___	The filtration system is sized for at least 1 gpm per living unit for transient or 3/4 gpm per living unit 
			for non-transient. (For multiple pools: cumulative total GPM, excluding spas, wading pools and
			interactive water features)

424.1.1	____ 	___/___	Conventional pool filtration system turnover period is not less than 3 hours unless otherwise 
	     	        	required. (For sizing purposes only.)

424.1.2.2.2	____ 	___/___	All pool walls (except steps and spa coves) have minimum 15' clearance  perpendicular to a 
	                   	tangent to the wall. (Interior step protrusion does not exceed 6’)

424.1.2.2.2	____ 	___/___	Corners shall be a minimum 90 degree angle.

424.1.2.2.2	____ 	___/___	Protruding corners to have at least 2" radius continued through top of gutter edge.
			Coping does not overhang into the pool more than 1-1/2”.

424.1.2.3.1 1.	____ 	___/___	Pool water depth is at least 3' in shallow area.

424.1.2.3.1 1.	____ 	___/___	Pool water depth is at least 4' in deep area.

424.1.2.2.2	____ 	___/___	The upper part of pool walls (areas of 5' or less depth) are within 5° of vertical for a minimum depth 
	                    	of 2½' and the radius joining this upper section to the floor does not exceed 2½'.

424.1.2.2.2	____ 	___/___	The upper part of pool walls in areas over 5' deep are within 5° of vertical for a minimum depth equal 
	                 	to the pool depth minus 2½' and the radius joining this upper section to the floor does not 
			exceed 2½'.

424.1.2.3.1 2.	____ 	___/___	Minimum 4" permanent contrasting depth markings, followed by the full or abbreviated words 
	                	"FEET" or "INCHES", properly located on both sides of the pool at shallow end, slope break, 
	                	deep end wall, and deep point.  Horizontal surfaces are slip resistant.
  
424.1.2.3.1 2.	____ 	___/___	Depth markers shall indicate actual depth within 3 inches.

424.1.2.3.1 2.	____	___/___	         Symmetrical pool designs with deep point at center have dual markings indicating depth at wall 
	                	and at the deep point, followed by FEET or INCHES.

424.1.2.3.1 3.	____	___/___	         Maximum perimeter distance between depth markings is 25'.

424.1.2.3.1 3.	____	___/___  Depth markings are visible from inside the pool and from the deck.

424.1.2.3.1 4.	____ 	___/___	When curb is provided, depth markings are located on inside and outside riser.  (Top of curb may be 
	               	substituted for outside riser location.)

424.1.2.3.1 4.	____ 	___/___	When no curb is provided, depth markings are located at or above water level on inside vertical 
	                	wall and on the deck (within 2' of water edge).

424.1.2.3.1 4.	____ 	___/___	When open type gutters are used, depth markers are located on the back of the gutter wall.

424.1.2.3.1 5.	____ 	___/___	When deck level perimeter overflow systems are used, additional depth markers are on 
	                	adjacent fencing or walls, large enough to be recognizable from inside the pool. Depth markers on
			deck are within 3' of water.  Or, depth markers may be at top of pool wall just under water level.

424.1.2.3.1 6.	____ 	___/___	In areas not part of an approved diving bowl, tile "NO DIVING" markings are on the curb top or deck 
	                	within 2' of water edge on each side of pool with a maximum distance between markings of 25'.

424.1.2.3.1 6.	____ 	___/___	The "NO DIVING" markings are at least 4" high and contrasting; or a 6” tile with min. 4” red 
			international “No Diving” symbol.

424.1.2.3.1 7.	____ 	___/___	All markings installed on horizontal surfaces have a slip-resistant finish.

424.1.2.3.1 7.	 ____	___/___  	All markings are tile (unless pool is fiberglass, thermoplastic or stainless steel).

424.1.2.2.3.2	____ 	___/___	Slope break (where applicable) has 5' depth or greater.

424.1.2.2.3.2	____ 	___/___	Slope break (if applicable) has 2-6" wide dark contrasting tile marking across bottom and up sides 
                                   			at the transition point.

424.1.2.2.3.2	____ 	___/___	Slope break (if applicable) has safety line mounted with recessed cup anchors 2' before contrasting 
                                   			marking, toward shallow end.

424.1.2.2.3.2	____ 	___/___	Safety line (if applicable) has visible floats at maximum 7' intervals.

424.1.2.2.3	____ 	___/___	Pool does not have double level floor.

424.1.2.2.3.1	____ 	___/___	The pool floor slope in areas of 5' depth or less does not exceed 1' in 10'.

424.1.2.2.3.1	____ 	___/___	The pool floor slope in areas of greater than 5' depth does not exceed 1' in 3'.

424.1.2.2.3.2	____ 	___/___	The transition from a pool floor slope of 1' in 10' to a greater floor slope has a slope break and 
	                	safety line.

424.1.2.2.3.1	____ 	___/___	The pool floor slope is at least 1' in 40'.

424.1.2.2.1	____    ___/___	Diving areas meet minimum requirements of the FINA Handbook 2005-2009.

424.1.2.5	____ 	___/___	Adequate number of steps, swimouts, recessed treads and/or ladders provided (Every 75' of  
	               	pool perimeter, minimum of 2) including both ends (plus deep point, if not at one end).  
			If deep end >30' wide, both sides have means of access.  

424.1.2.5.3	____ 	___/___	Pool steps have not less than 24" tread length(s), 10" tread width(s) nor more than 10" tread riser(s).  
	                	Max. tread width is 48”.

424.1.2.5.3	____ 	___/___	Intermediate step treads and risers are uniform in width and height (within ½”).

424.1.2.5.3	____ 	___/___ 	Dark, contrasting, slip resistant tiles are provided for intersection of tread and riser for entire length 
	                	of each step. (3/4” -2” on tread, 2” on riser, or slip resistant bullnose)

424.1.2.5.3	____    ___/___	Step and bench seat edge markings on vinyl liner and fiberglass pools are permanent, 
				permanently secured, dark, non-fading and slip resistant.

424.1.2.5.4	______ 	___/___	Swimouts extend 18" to 24" back from the pool wall and are 4' to 5' wide.

424.1.2.5.4	____ 	___/___	Unless stairs are provided, the swimout is a maximum of 12" below the deck.

424.1.2.5.4	____ 	___/___	Swimout is located in an area of the pool with a depth exceeding 5'.

424.1.2.5.4	____ 	___/___	If pool is on skimmers, a wall inlet is provided within the swimout.

424.1.2.5.4	____ 	___/___	A dark, contrasting colored, slip resistant tile band is located along the intersection of the pool wall 
                                  			and the swimout, extending 2" on horizontal and vertical surfaces.  Bullnose tile may be 
                                  			used with ¾” on horizontal surface.

424.1.2.5.5	____ 	___/___	Handrail(s) for the stairs are correct length to mount in deck and bottom step (figure four mounted in
				deck  and extended over bottom step).

424.1.2.5.5	____ 	___/___	Handrails shall extend between 28" and 40” above the step or deck.

424.1.2.5.6	____ 	___/___	If provided, lifts to accommodate handicapped persons have a four foot wide deck behind the 
	               	lift mount.

424.1.2.5.1	____ 	___/___	Ladder(s) are cross-braced, corrosion resistant, are the correct length to mount in pool deck, 
		        	extend 28" to 40” above deck, and extend over into pool.

424.1.2.5.1	____ 	___/___	Ladder treads are slip-resistant and the clearance between the ladder and pool wall is 3 to 6".  
	                	Ladder bottom braces have end caps.  Top rung is at or below water level on open gutter pools and 
				max. 12” below deck/curb top on all others. 

424.1.2.5.2	____ 	___/___	Step treads installed into pool wall shall be flush with pool wall and have minimum 5" tread width, 
	                	minimum 10" length, & a maximum vertical distance of 12" between steps.
		        
424.1.2.5.2	____ 	___/___	Step treads installed into pool wall have a grabrail at each side of the steps and each grabrail is 
		        	mounted in the deck and extends 28" to 40” above the deck.

424.1.2.6	____ 	___/___	Underwater bench seats are 14" to 18" wide and have a 2" wide dark contrasting slip resistant 
		       	tile marking along the horizontal and vertical surface.  Slip resistant bullnose tile may be used
                                 			 	with ¾” on horizontal surface.

424.1.2.6	____ 	___/___	Underwater bench seats are in areas less than five feet deep.

424.1.2.6	____	___/___	Benches do not protrude into the 15’ clearance requirement.

424.1.3.1.3 &.2      ____ 	___/___	Pool deck has unobstructed area with minimum 4' width around perimeter of pool, handrail 
		        	& ladder anchors, diving boards/towers, and slides. Pits and crevices more than 3/16” deep not 			allowed.

424.1.3.1.1	____ 	___/___	Pool deck constructed of impervious material with slip-resistant finish.

424.1.3.1.2	____ 	___/___	Pool deck is not below maximum 10" from the curb top when curb is provided.

424.1.3.1.2	____ 	___/___	Indoor and outdoor pool deck has a minimum 2% and maximum 4% uniform slope away from pool 	        		or to deck drains.

424.1.3.1.4	____ 	___/___	Traffic barriers provided to prevent obstruction of deck by vehicles (where applicable).

424.1.3.1.5 	____ 	___/___	Hose bibb with vacuum breaker is provided to wash deck with potable water.

424.1.3.1.5	____ 	___/___	Walkways between the pool and sanitary facilities are constructed of concrete or other
		         	non-absorbent materials for the first 15' of walkway and have a slip-resistant finish.

424.1.2.6	____ 	___/___	Pool water area has no obstruction.

424.1.2.6	____ 	___/___	Structures located inside pool perimeter are additional part of the recirculation system and  are not 
		        	located less than 15' from any pool wall and are not located within the diving bowl area.
		        
424.1.3.1.8	____ 	___/___	The vertical clearance above the pool deck is at least 7'.

424.1.3.1.6	____ 	___/___	Obstructions of the perimeter of the pool do not exceed 10% of total pool perimeter, and are 
			protected by a barrier or designed to discourage patron access.

424.1.3.1.6	____ 	___/___	Obstructions of the perimeter of the pool have a wet deck area behind or through the obstruction 
			and within 15'of the water edge. Approved slides have the near edge of walk within 35’ of water.
                                  		
424.1.3.2	_____ 	___/___	Bridge or obstruction over pool is at least 8' above pool bottom and at least 4' above water surface.

424.1.3.2	____ 	___/___	Minimum 42" high handrails are provided along each side of the bridge.

424.1.3.2	____ 	___/___	Bridge or walkway footing surface is constructed of concrete or other non-absorbent material 
			having a smooth slip-resistant finish.

424.1.6.5.3.1	____ 	___/___	Pool has perimeter overflow gutter or recessed automatic surface skimmers (where 			              		 allowed).
			
424.1.6.5.3.1	____ 	___/___	Overflow gutter lip is level(max. ¼” between high & low) and bottom of gutter is level or  
                                  			slopes to gutter drains.

424.1.6.5.3.1	____ 	___/___ 	The gutter drain spacing does not exceed 10' for 2" drains or 15' for 2½" drains.

424.1.6.5.3.1	____ 	___/___ 	Gutters may be eliminated for no more than 15’ of pool perimeter (or max.10% of perimeter). In such  			areas, handholds shall be installed within 9 inches of water surface.

424.1.6.5.3.1.3	____ 	 ___/___	Gutter lip has min. 2” of tile on pool wall (except if stainless steel). (tiles are min. 1” on all sides) 

424.1.6.5.3.1.1	____ 	 ___/___	Recessed gutter is at least 4" deep and 4" wide with no part of the gutter trough visible from a 
						point directly above.

424.1.6.5.3.1.1	____ 	 ___/___	Open type gutter is at least 6" deep and 12" wide with a 2" (± ¼") slope from the lip to the gutter 						drain level (may be 1” at steps if gutter used as tread) and back wall is smooth glazed tile.

424.1.6.5.3.1.1	___    __/__		Back of gutter drain is within ¾” of back vertical wall of gutter wall where gutter is deepest, 
						and flush or recessed no more than 3/8”.

424.1.6.5.3	____ 	 ___/___	Gutter drain system is capable of handling 100% of the recirculation flow and shall discharge 
						into the collector tank.

424.1.6.5.3.2	____ 	 ___/___	Skimmer pool water surface area does not exceed 1000 ft.² (excluding offset stairs & swimout) and 
					   does not exceed maximum width of 20' (when measured perpendicular to a tangent to the wall).

424.1.6.5.1	____ 	 ___/___	Skimmers have NSF approval.

424.1.6.5.3.2.1	____ 	___/___ 	Skimmer system designed to carry 60% of pool total design flow rate with each skimmer carrying 
					at least 30 gpm.

424.1.6.5.3.2.1	____ 	___/___ 	Number of skimmers is based upon 1 for every 400 ft.² or fraction thereof of pool water surface area.
			
424.1.6.5.3.2.2	____ 	___/___	 	Skimmers are located to take advantage of prevailing wind direction and to minimize interference 
						from adjacent inlets or skimmers.

424.1.6.5.3.2.2	____ 	___/___ 	Skimmers do not protrude into pool area.

424.1.6.5.3.2.2	____ 	___/___ 	Pools with skimmers have handhold in deck or curb construction which is not more than 9" above
			 			midpoint of skimmer.

424.1.6.5.3.2.3	____ 	___/___ 	Skimmer installation may be installed with spring loaded vertical check equalizer valve and 2” min.  
					 	diameter equalizer line, installed at least 12 “ below normal water level protected by an ASME/ANSI 						A112.19.8-2007 compliant grate, when skimmer system is connected to pump suction.  No float 						valves allowed.

424.1.6.5.3.2.4	____ 	___/___	A wall inlet fitting is directly across from each skimmer.

424.1.6.5.11	____ 	___/___	Pool makeup water supply is from an approved potable water system or meets those requirements 
			with bacteriological/chemical reports to county health department.

424.1.6.5.11	____ 	___/___	Pool makeup water supply has air break or approved backflow prevention device.

424.1.6.1.4&	____ 	___/___	Hose bibbs have vacuum breakers.
424.1.3.1.5

424.1.6.5.2	____ 	___/___	The recirculation/filtration equipment is designed to provide at least 4 turnovers of the pool volume
			 per day. Health or fitness centers shall provide 8 turnovers per day unless pool is 1000 ft² or larger.

424.1.6.5.3	____ 	___/___	The design pattern of recirculation flow of pool with overflow gutters is
			100% through main drain piping and 100% through gutter system piping.

424.1.6.5.3	____ 	___/___	The design pattern of recirculation flow for pool with skimmers is 100% through
			main drain and 60% through skimmer system piping.

424.1.6.10.5	____ 	___/___	A collector tank with an effective capacity of at least 1 minute of the design flow is provided.
			
424.1.6.5.11	____ 	___/___	An automatic water makeup control and a manual pool fillspout are provided to
			discharge into the collector tank with an air gap.

424.1.6.5.4	____ 	___/___	The recirculation pump is sized at the proper T.D.H. according to the type of filter system.
			
424.1.6.5.4	____ 	___/___	The recirculation pump (when mounted above the water level of the pool) is specified as self-priming.

64E-9.007(17)	____	___/___	Waterfalls or features: Return piping is capable of handling additional feature flow when feature 
                                 			turned off. Feature requiring more than 20% of flow rate has additional pump that drafts from 
                                 			a suitable collector tank.  Feature water is not  counted toward designed turnover rate.  
                                 			Water from the features returns to the pool.

64E-9.007(17)	____	___/___	Spray features mounted in deck are flush with pool deck.

424.1.6.5.9.6	____ 	___/___	The number of inlets handle the recirculation flow with a maximum flow of 20 gpm per inlet.
			
424.1.6.5.9	____ 	___/___	Wall return inlets are directionally adjustable and do not protrude into the pool.
                                   			Wall inlets are a min. of 12” below normal water level unless otherwise justified.

424.1.6.5.9.1	____ 	___/___	Pools 30' or less wide, with wall inlets only, have maximum spacing of 20' between inlets 
			based on pool perimeter.

424.1.6.5.9.2	____ 	___/___	Pools 30' or less wide, with floor inlets only, have inlets located such that they are not over 20' apart 
			nor over 10' from adjacent walls.

424.1.6.5.9.3	____ 	___/___	Pools 30' or less wide with combination floor and wall inlets meet requirements of
			either 424.1.6.5.9.1 or .2.

424.1.6.5.9.4	____ 	___/___	Pools greater that 30’ wide have floor inlets only or a combination of floor and wall inlets.

424.1.6.5.9.4	____ 	___/___	Pools greater than 30' wide, with floor inlets only, have inlets located such that they are not over 
			20' apart or 10' from adjacent walls.

424.1.6.5.9.5	____ 	___/___	Pools greater than 30' wide with combination floor and wall inlets have wall inlets not over 20' apart 
			(based on pool perimeter) and floor inlets are provided for the water area beyond 15' perpendicular
			distance from all walls.  (Floor inlets are located not over 20' apart and 25' from adjacent walls.)

424.1.6.5.9	____ 	___/___	Floor return inlets have a means of flow adjustment.

424.1.6.5.9	____ 	___/___	Floor inlets do not protrude above pool floor and do not have sharp edges or protrusions.  For
			vinyl liner & fiberglass pools, floor inlets are not more than 3/8” above floor. 
                                  
424.1.6.5.10	____ 	___/___	The main drain grate(s) are located at the deepest point in the pool and are flat, flush, and
			 not readily breakable or removable by bathers.

424.1.6.5.10.1	____ 	___/___	The depth at the deepest point/main drain grate does not deviate more than 3" from side wall depth 
 			indicated by depth markers at the location. (unless dual marking used)
                                   
424.1.6.5.10.2	____ 	___/___	The open area of the main drain grate(s) is such that the flow velocity at the grate(s) does not 
			exceed 1½' per second at the design flow rate of the recirculation pump.
                                   
424.1.6.5.10.3	____ 	___/___	Pool over 30' wide in deep end has multiple main drain grates, equally spaced from the pool 
			side walls and each other.

424.1.6.5.10.4	____ 	___/___	Hydrostatic relief devices have been provided if high ground water exists at site.

424.1.6.5.4	____ 	___/___	If the recirculation pump takes suction prior to filtration, the pump is specified with hair and 
			lint strainer.

424.1.6.5.12	____ 	___/___	A portable or plumbed vacuuming system is provided which allows vacuuming the pool with a hose 
			not more than 50' in length. Recirculation pump over 3 hp is not used for vacuuming.
                                   
424.1.6.5.12	____ 	___/___	Vacuum cleaning system pump is provided with hair and lint strainer.

424.1.6.5.12	____ 	___/___	A vacuum fitting with spring-loaded safety cover, is flush mounted no more than 15” below water
			level. (12” acceptable in FBC, 15” max. per 64E-9.007(12).

424.1.6.5.12	____ 	___/___	Bag type cleaners that operate as ejectors on potable water supply pressure
			are protected by a vacuum breaker.

424.1.6.5.13	____ 	___/___	A flowmeter capable of reading at least 1½ times the design flow rate is properly located with
			proper clearances upstream and downstream.  (Located in the pump discharge line
			for sand filter systems and in the pool return line for other filter systems.)
			
424.1.6.5.14	____ 	___/___	If heater is provided, a fixed thermometer is mounted in the pool recirculation line
			downstream of the heater outlet line connection.

424.1.6.5.14	____ 	___/___	Sufficient valves and piping are provided to allow isolation or removal of the pool heater.
			
424.1.6.5.14	____ 	___/___	Heater bypass valve is designed for proportioning flow (gate valve is unacceptable).
			
424.1.6.5.14	____ 	___/___	Material used in solar and other heaters are non-toxic and acceptable for potable water use.
			
424.1.6.5.6	____ 	___/___	Plastic pipe has NSF-pw seal of approval and is completely specified.

424.1.6.5.6	____ 	___/___	Plastic pipe exposed to sunlight is coated for UV protection.

424.1.6.5.7	____ 	___/___	Return line, main drain line, and surface overflow system lines each have proportioning valves.

424.1.6.5.8	____ 	___/___	All pressure piping is sized such that the flow velocity does not exceed 10' per second at the 
			design flow rate.  (Exception for precoat lines when higher velocity is needed for agitation purposes.)
			
424.1.6.5.8	____ 	___/___	All suction piping is sized such that the flow velocity does not exceed 6' per second at the design 
			flow rate.  (Exception is vacuum filter header assembly where velocity may be up to 10' per second.)
			
424.1.6.5.8	____ 	___/___	Main drain systems and surface overflow systems which discharge to collector tanks are sized

such that the flow velocity does not exceed 3' per second at the design pattern of recirculation flow.

424.1.6.5.15	____ 	___/___	Each waste line has a unique air gap and is not connected to other lines.  Method of water 
                                  			& DE powder disposal is acceptable.

424.1.6.5.5.1	____ 	___/___	Sand filters:  The filter is sized such that the filtration rate does not exceed 3 gpm/ft² for rapid
			sand filter or 15 gpm/ft² for high rate sand filters (or 20 if so rated by NSF).

424.1.6.5.1	____ 	___/___	Sand filters meet the requirements of NSF/ANSI Standard 50 - 2007.

64E-9.007(8)	____ 	___/___	Sand filters:  The recirculation pump(s) and piping is designed to be capable of backwashing.

424.1.6.5.4	____ 	___/___	Sand filters:  The recirculation pump provides a min. T.D.H. of 60' for filtration unless hydraulically 
			justified by the design engineer.

424.1.6.5.5.2.1	____ 	___/___	Sand filters:  Pressure filters have influent and effluent pressure gauges with minimum 2" face 
			diameter(s) and scale(s) of 0-60 psi and a sight glass in the backwash line.

424.1.6.5.5.2.1	____ 	___/___	Sand filters:  The pressure filter tanks have air relief valves.

424.1.6.5.5.2.2	____ 	___/___	Sand filters:  Vacuum filter has 2", or larger, diameter vacuum gauge in suction line with 0-30" 
			(mercury) scale.

64E-9.007(8)	____ 	___/___	Sand filters:  Piping system permits filtering to pool, vacuuming to filter, vacuuming to waste, 
                                   			backwashing individual filters, complete drainage of the system, and space to allow maintenance.

424.1.6.5.5.1	____ 	___/___	D.E. Type filters:  The filter is sized such that the filtration rate does not  exceed 2 gpm/ft².

424.1.6.5.5.2.3	____ 	___/___	If diatomaceous earth type filters are used, separation devices are provided and properly sized 
			for the waste water system.

424.1.6.5.1	____ 	___/___ 	D.E. type filters:  Components and materials have been tested and approved using 
			NSF/ANSI Standard 50-2007.

424.1.6.5.5.2.3	____ 	___/___	D.E. type filters:  Pressure filter(s) have precoat pot or collector tank for precoating purposes.

64E-9.007(8)	____ 	___/___	D.E. type filters:  Pressure filter(s) have piping to backwash to waste by reverse flow procedure 
			and filter can be completely drained.

64E-9.007(5)(c)	____ 	___/___	Custom design filter meets the requirements of 64E-9.007(5)(c).

424.1.6.5.5.3	____ 	___/___	D.E. type filters:  The filter area is determined on the basis of effective filtering surfaces  with no 
			allowance given for areas of impaired filtration.

424.1.6.5.5.3	____ 	___/___	D.E. type filters:  Filter septa have a minimum 1" clear spacing between elements (up to 4 ft² effective
			area per septum) and the minimum spacing between elements is 1/8" larger for each additional 
			square foot or fraction thereof of septum area over 4 ft².

424.1.6.5.4	____ 	___/___	D.E. type filters:  The recirculation pump provides 60' T.D.H. for pressure systems and 50' T.D.H. 
                                 			for vacuum systems.
			
424.1.6.5.5.2.1	____ 	___/___	D.E.  type filters:  Pressure filter(s) are equipped with air relief valves, influent/effluent pressure 
			gauges (2" minimum face diameter), and a sight glass in the waste line.
			
424.1.6.5.5.2.2	____ 	___/___	D.E. type filters:  Vacuum filter has vacuum gauge with minimum face diameter of 2", reading 0-30"
			of mercury located on suction line.
			
424.1.6.5.5.3	____ 	___/___	D.E. type filters:  Vacuum filter tank has coved intersections between the wall and the floor and the
			 tank floor slopes to the filter tank drain.

64E-9.007(8)	____ 	___/___	D.E. type filters: The system allows filtering to pool, precoat recirculation to filter, vacuuming to
			waste, vacuuming to filter, backwashing (pressure filter) to waste, and complete drainage of filter 
			tank.

424.1.6.5.5.1	____ 	___/___	Cartridge filters:  The filter complies with the maximum filtration rate of 0.375 gpm/ft² for pleated 
			type cartridges.

424.1.6.5.1	____ 	___/___	Cartridge filters: The filter model has met the requirements of NSF/ANSI Standard 50-2007.

424.1.6.5.4	____ 	___/___	Cartridge filters:  The recirculation pump is selected to give 60' T.D.H.

424.1.6.5.5.2.1	____ 	___/___	Cartridge filters:  Pressure type filter(s) are self-purging or have air relief valves and have 
			influent/effluent pressure gauges with minimum 2" face diameters and reading 0-60 psi.
			
424.1.6.5.5.2.2	____ 	___/___	Cartridge filters:  Vacuum filter has vacuum gauge with 2" minimum face 
			diameter (0-30" mercury reading) located on the suction line.

64E-9.007(8)   	____ 	___/___	Cartridge filters:  Filter system is capable of filtering to pool, vacuuming to waste, vacuuming to
			 filter, and complete drainage of the filter tank with space for maintenance.
			
64E-9.007(5)(c)	____ 	___/___	Cartridge filters:  The filter cartridges are permanently marked with the
			manufacturer's name, pore size, and filter area on one end cap.

424.1.6.5.16.2	____ 	___/___	Hypohalogenation:  The feeder has adjustable feed rate from zero to full range
			and meets the requirements of NSF/ANSI Standard 50-2007.

424.1.6.5.16.2	____ 	___/___	Hypohalogenation:  The feeder is capable of feeding a dosage of 6 ppm to the minimum required 
			turnover flow rate (if solution type feeders, a 5% calcium hypochlorite or 10% sodium hypochlorite
			solution).

424.1.6.5.16.2	____ 	___/___	Hypohalogenation:  An electrical feeder, when used, has electrical interlock
			with the recirculation pump.  A flow sensor controller may be used.

424.1.6.5.16.2	____ 	___/___	Hypohalogenation:  Solution crock has a volume equal to at least 50% of the
			maximum daily feed capacity of the chlorine solution feeder.

424.1.6.5.16.2	____ 	___/___	Hypohalogenation:  Solution crock is marked to indicate contents.

424.1.6.5.16.2	____ 	___/___	Erosion type feeder shall have a flowmeter and flow adjustment valve.

424.1.6.5.16.3	____ 	___/___	pH adjustment feeder:  A positive displacement type feeder adjustable from
			zero to full range & meets NSF/ANSI Standard 50-2007 is provided.

424.1.6.5.16.3	____ 	___/___	pH adjustment feeder:  An electrical feeder has electrical interlock with the recirculation pump.
			
424.1.6.5.16.3	____ 	___/___	pH adjustment feeder:  The solution crock volume is at least 50% of the maximum
			daily capacity of the feeder and is marked to indicate the contents.

64E-9.004(11)	____ 	___/___	A test kit is provided and is capable of testing for free active halogens,
			total or combined available chlorine, total alkalinity, calcium hardness & pH.

64E-9.004(11)(a)	____ 	___/___	If a cyanurate type feeder is used, a cyanuric acid test kit is provided.

64E-9.004(11)(a)	____ 	___/___	If a salt solution in the pool water is necessary for a chlorine generator, a sodium chloride test kit 
			is provided.

424.1.5.1	____ 	___/___	An equipment room or enclosure is provided which is protected from unauthorized entrance
			and from the weather on 3 sides and overhead.  Equipment designated by manufacturer for 
			outdoor use may be located in a 4’ min. fenced equipment area with self-closing, self-latching 
                                   			gate with locking device.

424.1.3.1.9			A gate through the pool fence from the pool area to the equipment area is provided within 10 feet of the equipment area is provided

424.1.5.3	____ 	___/___	The equipment room floor is constructed of concrete or other nonabsorbent material having a 
			smooth slip-resistant finish and uniformly sloped to prevent standing water.
			
424.1.5.4	____ 	___/___	The equipment room has forced draft, or adequate cross ventilation, and positive floor drainage 
       			with sump pump if needed.

424.1.5.4	____ 	___/___	Below grade equipment rooms have a stairway with forced draft ventilation or fully louvered door 
			and powered intake within 6” of floor.  Ship’s ladder may be specified by design engineer.

424.1.5.5	____ 	___/___	The equipment room access is at least 3' x 6'.

424.1.5.9	____ 	___/___	The equipment room is provided with a hose bibb with vacuum breaker.

424.1.5.6	____ 	___/___	The equipment room size and layout provides clearances for all equipment as
			prescribed by the manufacturer to allow normal maintenance and removal.

424.1.5.6	____ 	___/___	The equipment room with a fixed ceiling has a minimum height of 7'.

424.1.5.7	____ 	___/___	The equipment room is lighted to provide a minimum 30 fc of illumination at floor level.

64E-9.006(2)(e)	____ 	___/___	Collector tank or filter tank (vacuum system) is not accessible to unauthorized individuals.

424.1.4.2	____ 	___/___	Lighting:  Artificial lighting is provided when natural lighting is not  adequate or when night 
			swimming will be allowed.

424.1.4.2.1	____ 	___/___	Outdoor pool lighting:  If night swimming is to be allowed, lighting will provide at least 3 fc 
			of illumination at the water and wet deck level.

424.1.4.2.1	____ 	___/___	Outdoor pool lighting:  If night swimming is to be allowed, underwater lighting will provide 
     			at least 1/2 watt per square foot of pool water surface area.  
			(Except where above water lighting is at least 15 fc of illumination.)

424.1.4.2.2	____ 	___/___	Indoor pool lighting:  If natural illumination is inadequate, or night swimming is to be allowed, 
			lighting shall provide at least 10 fc of illumination at the water and wet deck level.

424.1.4.2.2	____ 	___/___	Indoor pool lighting:  If natural illumination is inadequate or night swimming  is to be allowed, 
      			underwater lighting will provide 0.8 watt per square foot of water surface area.  (Except where 
			above water level lighting is at least 15 fc of illumination.)

424.1.4.2.3	____ 	___/___	Lighting:  The underwater lighting utilizes transformers and low voltage  circuits (15 volts maximum) 
			with each underwater light grounded.  (When dependent upon submersion for safe operation, 
			lights have protection from overheating when not submerged.)
			
424.1.4.2.3	____ 	___/___	Lighting:  The underwater incandescent lamp size does not exceed 300 watts and is located
			at least 18" below normal water level. (center line of skimmer, or  top lip of gutter)


424.1.4.2.4	____ 	___/___	Lighting:  The plans do not show overhead service wiring within 10' horizontally of the pool walls or 
			deck appurtenances; or clearances meet NEC standards.

424.1.4.1	____ 	___/___	The electrical equipment wiring and installation will conform to the Chapter 27, of the Florida Building
 			Code, Building.

424.1.1	____ 	___/___	Bathing load:  If the pool is not a spa pool, the bathing load is computed on the basis of 1 person       			per each 5 gpm of water recirculated.

424.1.1	____ 	___/___	If the pool is a spa, the bathing load is computed on the basis of 1 person per each 10 ft² of 
			water surface area.

64E-9.008(7)	____    ___/___	The bathing load will be posted at the pool as required in the bathing rules.

424.1.6.1	____    ___/___	If bathing load is less than 40, Separate sanitary facilities for each sex are provided, entrances

Are labeled for men or women, and entry doors are within 200' walking distance of the nearest

water's  edge for each pool.

424.1.6.1.1	____    ___/___	Fixtures are provided as indicated on the following chart:  (suitable for deck area up to 3x pool
		surface)

	                      Men's Restroom                                                Women's Restroom
	     Size           Urinals      WC     Lavatory                         Size              WC     Lavatory
	0-2500 ft²           1             1            1          	0-2500 ft²              1           1
	2501-5000 ft²     2             1            1          	2501-5000 ft²        5           1
	5001-7500 ft²     2             2            2         	5001-7500 ft²        6           2
	7501-10,000 ft²  3             2            3          	7501-10,000 ft²     8           3

424.1.6.1.1  	____   ___/___ 	Supplemental family-style restrooms may be used to meet requirements.

424.1.6.1  	____   ___/___ 	Unisex restrooms: may be used if bathing load is 20 or less (1), or 40 or less (2).
	                              Each has a water closet, a urinal, a lavatory and a diaper changing table.

424.1.6.1  	____ 	___/___	Pools greater than 10,000 ft² have one additional fixture set for each 7,500 ft² or major fraction           			thereof above 10,000 ft², and meet 3:2 female/male ratio requirements.  Lavatory counts are equal.

424.1.6.2	____ 	___/___	Sanitary facilities for outdoor pool have outside access door.  If in adjacent building, 
			doors are within 50’ of the exterior door.  

424.1.6.1	____ 	___/___	Sanitary facilities are not required if all units served by the pool are within a 200' horizontal radius
exception			from the nearest pool water edge, are not over 3 stories high, unless served by elevator, and have
			private sanitary facilities.

424.1.6.1.3	____ 	___/___	Sanitary facilities' floors are to be constructed of concrete or other impervious material and have a 
			smooth, slip-resistant finish.

424.1.6.1.3	____ 	___/___	Sanitary facilities' floors are sloped for positive drainage to drains.

424.1.6.1.3	____ 	___/___	Intersections between floors and walls are coved if either floor or wall isn’t waterproof material.

424.1.6.1.3	____ 	___/___	Sanitary facilities: There are no foot baths, carpet or duck boards on the floor.

424.1.6.1.4	____  	___/___	A hose bibb with vacuum breaker is in or within 25’ each restroom for ease of cleaning.

424.1.6.1.2	____ 	___/___	Sanitary facilities:  Where separate non-private sanitary facilities are provided and are not visible 
			from any portion of the pool deck, signs are  posted showing directions to the facilities. 
			Signs are legible from the pool deck, with letters at least 1" high.

424.1.6.1.1	____	___/___	One diaper changing table is provided at each restroom unless all pools restricted to adult use.

424.1.6.2	____ 	___/___	If the pool is outdoors, a rinse shower is provided on the pool deck and is located within 20' of 
			the pool water edge.

64E-9.008(2)	____ 	___/___	If the pool length is 50' or less, at least 1 shepherd's hook with one-piece pole (minimum 16' long) 
			and 1 lifesaving ring (minimum 18" in diameter) with  sufficient rope attached to reach all parts 
			of the pool from the deck are provided, mounted in a conspicuous place.

64E-9.008(2)	____ 	___/___	If the pool length is greater than 50' there are multiple shepherd's hooks with one-piece poles 
			(min. 16' long) and multiple lifesaving rings (min. 18" diameter) with sufficient ropes attached to 
			reach all parts of  the pool from the deck, mounted along each of the longer sides of the pool.

64E-9.006(1)(e)	____ 	___/___	There are no protrusions, extensions, means of entanglement, or other obstructions on the pool 
			floor or pool walls.
			
64E-9.008(4)	____ 	___/___	If solar blanket or pool cover is specified, it is either secured around entire  pool perimeter and 
			can support a live load of an adult person, or the pool area  can be made inaccessible to
			unauthorized persons when cover is in use.

424.1.3.1.9	____	___/___	Pool is surrounded by min. 48” high fence with self-closing, self-latching, lockable gates opening 
			away from pool.  Latch is 54” above bottom of gate or min. 3” below the top of the gate on  the pool 
			side.  Fence does not allow passage of 4” diameter sphere.  Locks, if self-locking, may be 34 - 48”           			above floor or ground.


424.1.3.1.9	____	___/____	Access through the fence from dwelling units is via minimum 48” self-closing,  self-latching, lockable      			gate. Doored access from public rooms need not be through gates.

424.1.3.1.9	____	___/___	Other substantial barriers may be considered by the department.

424.1.3.1.9	____      ___/___	Screened pool enclosures are hardened on the bottom 3 feet.

424.1.5.8	____ 	___/___	Provision is made for storage of chemicals in well-ventilated area: 64E-9.008(5) adds: under roof 
			and protected from access by unauthorized persons.
 
64E-9.008(6)	____ 	___/___	Swimming pool slide is installed in accordance with the manufacturer's specification.

424.1.6.5.11	____ 	___/___	Over the rim fill spout prohibited.

64E-9.008(7)	____ 	___/___	The following rules will be posted at or near poolside and will be legible from pool deck:
			1.  No food or beverages in pool or on wet deck.
			2.  No glass or animals within fenced pool area (or 50’ from unfenced pool ).
			3.  Bathing Load:____persons.
			4.  Pool Hours: ____A.M. to ____P.M.
			5.  Shower before entering pool.
			6.  Do not swallow the pool water.

64E-9.008(7)	____ 	___/___	The lettering for the pool rules sign is at least 1" high.

64E-9.008(7)	____ 	___/___	Pool over 200 ft² without an approved diving bowl configuration has "NO DIVING" 
			included on the pool rules in lettering at least 4" high.

424.1.3.1.7	____	___/___	There is no provision for drink or food serving facilities within 12’ of the water’s edge.